usvd documentation

What is usvd and where does the name come from?

-----------------------------------------------

usvd is a highly configurable daemon which watches a power supply state

and reacts upon state changes (i.e. line fail, line back, battery low

situations). The term "usv" is the abbreviation of

"Ununterbrochene Spannungs-Versorgung" which is the German translation

of "uninterrupted power supply".

It is quite similar to genpower by Tom Webster (though independently

developed) except that usvd does not need SYSVINIT and does not interact

with it. This makes it useful for Linux distributions without SYSVINIT

or such with a very different/non-standard setup.

Making a cable to connect the power supply

------------------------------------------

Most power supply devices provide relay contacts that indicate the current

state. You must look into the manual of your power supply and build a

special cable.

Warning: It is not recommended to use any power supply that does not

provide relay contacts. Some devices with modern analog switches instead

of a relay didn't work for me. Using a relay is most safe from the

electrical point of view anyway since the circuits are completely

seperated.

usvd and usv_off use the following signals on a serial port:

DCD high = line fails

DSR high = line okay, must be NOT(DCD) otherwise the connection is broken

CTS high = battery is low

RTS is set to high when usvd is running (+12V for relais contacts)

DTR is set to high for 1 sec. when the power supply is to shut down

GND Ground for the signals

Warning: 9-pin and 25-pin serial connectors at the computer have very

different pin assignments. Refer to the following cable.

DCD    DSR    CTS    RTS    DTR    GND

9-pin        1      6      8      7      4      5

25-pin       8      6      5      4     20      7

The daemon has been written for power supply devices that have the

following relay contacts. Connect the pins of the computer's serial

port as follows:

o---  DSR (line okay)

/  <------------ indicates "line ok" situation

(+12V) RTS  ---o

o---  DCD (line fail)

/  <---- open when battery okay, close when low

(+12V) RTS  ---o   o---  CTS (battery low)

Also the power supply has a shutdown contact (i.e. it can be switched off

by the computer):

DTR -----o  Shutdown contact (power supply shuts down

GND -|<|-o  when it receives a pos. pulse here)

^diode (in most cases not necessary, connect

the pins directly instead)

Some people strongly recommend to use additional resistors in the cable.

From the electrical point of view they are not necessary, but in case of

error they might prevent electrical damage (though it's very unlikely to

damage a relay contact even in case of error...)

If your power supply looks different here, you'll have to use your phantasy

how to do it. Feel free to adapt the usvd.c and usv_off.c sources for your

purpose.

Configuring the software

------------------------

Compile the programs usvd and usv_off by running 'make' and 'make install'.

The binaries are copied to the /sbin directory.

Run usvd from your bootup script and usv_off from your shutdown script

(note that the power supply is *off* after running usv_off if the line

has failed). Be sure to know what you do here and keep a boot/root rescue

disk pair. It's easy to make mistakes which may make your system refuse to

boot up correctly. Since almost each Linux distribution uses different

startup and shutdown scripts I cannot tell exactly what to change :)

Slackware: startup script: /etc/rc.d/rc.M

shutdown script: /etc/rc.d/rc.0

Suse: startup script: choose one in /sbin/init.d/*

shutdown script: /sbin/init.d/halt

Create a link in /dev that points to the serial port your usv is connected

to:

cd /dev

ln -s ttyS1 usv

usvd monitors the power state every 10 secs via the serial line.

usv_off switches the power supply off only when it signals line failure -

otherwise it doesn't do anything (so you can reboot as usual).

Create these script files:

/etc/usvd/linefail: This script is executed once when usvd detects line

failure. It should send a warning to all users currently

on the system (see 'man wall'). You may also initiate

'shutdown in some minutes' here if you want. See hint

below.

/etc/usvd/lineback: This script is executed when the power comes back before

the system has shutdown. It usually cancels a shutdown

initiated by linefail and informs the users ('man wall').

/etc/usvd/battlow:  This script is executed when usvd receives the battery

low signal. It should immediately start system shutdown.

/etc/usvd/noconnect:This script is executed when usvd finds contradicting

conditions. This usually means someone has disconnected

the serial cable.

It's up to you to decide what to do in the different situations. Customize

your scripts according to your local requirements. There are example

files in the etc subdirectory.

HINT: If you want to initiate a shutdown, put the shutdown command in the

background. So you can cancel it if power comes back in time.

Otherwise usvd may be blocked and thus cannot receive the power-ok

signal.

When is a more complex setup useful?

-------------------------------------

Just imagine you have a local network with two servers carrying important and

valueable data. Both are plugged into the power supply's outlet. But only

one server can monitor the power supply state. It might be useful if this

server halts the other one in case of line failure via the network.

You can also send mails to the system administrator on power failure.

If you have a modem and fax software running, you can even try to send a

'cry for help fax'.

But please note that your network transceiver, hub or modem should also

be connected to the power supply - otherwise it would not be very useful

in a power fail situation :)

Author

------

This package has been written by Frank Gockel. It is distributed under the

Gnu General Public Licence.

If you want to contact me via email please write in English or German to

gockel@sent13.uni-duisburg.de.